PLUMBING INSPECTIONS REQUIRED FOR

NEW CONSTRUCTION

Plumber must call at least 24 hours in advance to schedule a plumbing inspection.  Plumber or homeowner MUST be present at time of inspection.

- Service Line (Inspector will check all connections.)

See Diagram for Meter Box to House Connections – back page

- Rough In (BEFORE slab is covered)

- Top Out (BEFORE sheet rock)

- Final Inspection

ARKANSAS DEPARTMENT OF HEALTH REQUIREMENTS

PLUMBING INSPECTION

Arkansas Department of Health regulations require all public water systems to set up a system of permits and inspections to insure that public health and safety is protected.

All plumbing defined in Section 17-31-101 of the Arkansas State Plumbing Code is required by law to be permitted and inspected.  For customers of the Madison County Water Facilities Board this includes the following:

- All plumbing work must be done by a licensed master plumber OR may be done by a property owner in a building owned and occupied by him/her as his/her home.

- Yard lines from the meter to the house must be buried a minimum of 24” deep and inspected before being covered.  No other lines to be buried with the water line.

- A threaded shut-off valve must be installed at the meter box.  Stop and waste valves are NOT permitted.

- A dual-ball check valve will be installed at the meter box, after the shut off valve.

- A pressure-reducing valve must be installed either at meter box or first usage at house.

- All connections to a well or other sources shall be physically disconnected from the public water supply.

- A safety inspection of all hot water heaters will be made to insure that a temperature and pressure relief valve and an expansion tank are installed properly and that a drain line is properly installed to drain outside the home.  An inspection will also be made to see that gas water heaters are vented properly.

- Types of pipe approved for yard lines are:

- Copper

- Polybutylene

- PVC Schedule 40

- Galvanized

- All plastic pipe shall have a minimum of 160-lb. pressure rating, 200 PSI preferred.

- Pex

- Types of pipe approved for inside of building for water:

- Pex

- Copper

Types of pipe approved for under concrete:

- Sleeved copper

- Pex

Type of pipe approved for drains inside of building:

- Schedule 40 PVC

- Type of fittings approved for drain line:

- All fittings used to change direction will have sweeps.  (No standard 90’s or 45’s)

Inspections on plumbing will be made by a Certified Plumbing Inspector provided by the Madison County Water Facilities Board at 479-738-2214.

Fees for the plumbing inspection will be $75.00.

ARKANSAS DEPARTMENT OF HEALTH REQUIREMENTS

SEPTIC SYSTEM INSPECTION

Inspection procedure:

- Check on presence of septic tank;

- Check on presence of lateral lines;

- Check as to proper function of entire system (i.e. if above-ground effluent is present).

If no system exists, a percolation test and design system must be done by a licensed individual.  A permit for construction must be obtained.

If system show malfunction, appropriate repairs must be made within 30 days.

Inspections will be made by a representative of the Arkansas Department of Health.  Call your County Sanitarian.  (Madison County Sanitarian: 479-738-2612; Washington County Sanitarian: 479-521-8181; Benton County Sanitarian: 479-986-1300)

HOUSE

OUTSIDE HYDRANT

CUSTOMER’S BOX

METER BOX

- DUAL BALL CHECK VALVE

- PRESSURE REGULATOR

- SHUT OFF VALVE (THREADED)

*CUSTOMER MAY INSTALL PRESSURE REGULATOR HERE OR AT HOUSE

¾” BRASS NIPPLE

w/ MALE THREADS